## !!__UserGuide
Modbus Section Definition
User Guide
Generalities
!!! Greyed out cells SHOULD not be edited by hand.
Doing so will erase the formula they contain.
SectionDef Columns
Section ID
The type identifier of the section
!!! The Section ID MUST be unique and ranged between 1 and 255
Section Name
The friendly of the section, without the "_vX" suffix.
!!! Case sensitive
Section Version
A version identifier for the section the check the modbus size
This field is just for manual check, and is not used in any automated generation process
Section MBSize
The size of the particular version of the section, in 16-bits modbus registers
Info
Section description
Won't be used by automated processing
Section Columns
Name
The name of the data.
Should be unique within a section, and preferable across all the different section
Type
The type of the data
Special case for the bytes array and strings, which must be noted byte$X or str$X, where X is the EVEN number of byte
!!! Odd X value will cause errors afterwards
MBSize
The number of 16-bits modbus registers required for this data
Offset
The offset of the data within the section
Mode
Access mode override for the data, override the section access mode
Let to default to use the table access mode
Factor & Exponent
Some scaling value, to be used by a modbus client to alter the raw data value
Intended to be used as:
Data_final = Data_raw * Factor * 10^Exponent
Empty factor is equal to 1
Empty Exponent is equal to 0
Unit
Data unit indication, to be used by a vizualizing tool
Min & Max
The minimum value of the data
Only applicable to numeric data
Left empty to use the natural data type limit
Default
The default value for this data
Description
A short description of the data
Won't be used by automated processing
Info
A detailled info about the data, bits/values meaning in case of bitfields or enum
Won't be used by automated processing
HOWTO Create a new section
Copy the sheet $__SectionTemplate and name it MYNEWSECTION, suffixed with _vX, where X is the version identifier of the section
Add the new section name in the list in the tab __SectionDef, then define an Section ID
!!! The Section ID MUST be unique and ranged between 1 and 255
In the MYSECTION_vX tab, add data to the list
Be sure to ends the data list with a not-named null-type data (as shown in the template section)
HOWTO Edit an existing section
Although editing an existing section is not recommended
(as a new version of this section should be created instead)
Just add the new data next to the already present ones
Be sure to ends the data list with a not-named null-type data (as shown in the template section)

## __SectionDef
Section ID | Section Name | Section Version | Section MBSize | Info
1 | __InfoHeader | 1 | 16 | Generic device info header
2 | __SectionList | 1 | 3 | Section Table
10 | EEM_MA370_part1 | 1 | 28
11 | EEM_MA370_part2 | 1 | 9
12 | OR_WE_514_part1 | 1 | 41
13 | OR_WE_514_part2 | 1 | 2
14 | SOLIS_4G_3P_part1 | 1 | 39
15 | JANITZA_B23_part1 | 1 | 22
16 | EASTRON_SDM630_part1 | 1 | 344

## __Types (hidden)
Allowed data types - !!! DO NOT EDIT
Name | Byte | MBSize
| 0 | 0
null | 0 | 0
uint8 | 1 | 1
uint16 | 2 | 1
uint32 | 4 | 2
uint64 | 8 | 4
int8 | 1 | 1
int16 | 2 | 1
int32 | 4 | 2
int64 | 8 | 4
bool | 1 | 1
float32 | 4 | 2
byte$* | $var | $var
str$* | $var | $var

## __AccessModes (hidden)
Allowed access modes - !!! DO NOT EDIT
Name
default
no
ro
wo
rw

## $__SectionTemplate
Name | Type | MBSize | Offset | Mode | Factor | Exponent | Unit | Min | Max | Default | Description | Info
reg1 | uint16 | 1 | 0 | default |  |  | V
reg2 | uint16 | 1 | 1 | default |  |  | A
reg3 | uint16 | 1 | 2 | default |  | -3 | A
reg4 | uint16 | 1 | 3 | default |  | -1 | degrC
reg5 | uint16 | 1 | 4 | default |  | -1 | Vrms
reg6 | uint16 | 1 | 5 | default | 0.5 | -3 | Wh
reg7 | uint16 | 1 | 6 | default
reg8 | uint16 | 1 | 7 | default
reg9 | uint16 | 1 | 8 | default
reg10 | uint16 | 1 | 9 | default
| null | 0 | 10
-1
-1
-1
-1
-1
-1

## __InfoHeader_v1
Name | Type | MBSize | Offset | Mode | Factor | Exponent | Unit | Min | Max | Default | Description | Info
usMbsMappingRev | uint16 | 1 | 0 | default
usSectionOffset | uint16 | 1 | 1 | default
usSectionCount | uint16 | 1 | 2 | default
rfu | uint16 | 1 | 3 | default
usHWDesigneID | uint16 | 1 | 4 | default
usHWBomRev | uint16 | 1 | 5 | default
usProdDate | uint16 | 1 | 6 | default
usProdSerial | uint16 | 1 | 7 | default
usSWVersion | uint16 | 1 | 8 | default
usBuildYear | uint16 | 1 | 9 | default
usBuildDate | uint16 | 1 | 10 | default
usBuildTime | uint16 | 1 | 11 | default
usGIT1 | uint16 | 1 | 12 | default
usGIT2 | uint16 | 1 | 13 | default
usGIT3 | uint16 | 1 | 14 | default
usGIT4 | uint16 | 1 | 15 | default
| null | 0 | 16
-1
-1
-1
-1
-1
-1

## __SectionList_v1
Name | Type | MBSize | Offset | Mode | Factor | Exponent | Unit | Min | Max | Default | Description | Info
Offset | uint16 | 1 | 0 | default
Length | uint16 | 1 | 1 | default
Type | uint16 | 1 | 2 | default
| null | 0 | 3
-1
-1
-1
-1
-1
-1

## EEM_MA370_part1_v1
Name | Type | MBSize | Offset | Mode | Factor | Exponent | Unit | Min | Max | Default | Description | Info
Vrms12 | float32 | 2 | 0 | default |  |  | V |  |  |  | Vrms L1
Vrms23 | float32 | 2 | 2 | default |  |  | V |  |  |  | Vrms L2
Vrms31 | float32 | 2 | 4 | default |  |  | V |  |  |  | Vrms L3
_stub | byte$12 | 6 | 6 | default
Freq | float32 | 2 | 12 | default |  |  | Hz |  |  |  | Frequency
Irms1 | float32 | 2 | 14 | default |  |  | A |  |  |  | Irms L1
Irms2 | float32 | 2 | 16 | default |  |  | A |  |  |  | Irms L2
Irms3 | float32 | 2 | 18 | default |  |  | A |  |  |  | Irms L3
_stub | byte$4 | 2 | 20 | default
APwr | float32 | 2 | 22 | default |  |  | W |  |  |  | Active power
RPwr | float32 | 2 | 24 | default |  |  | VAR |  |  |  | Reactive power
SPwr | float32 | 2 | 26 | default |  |  | VA |  |  |  | Apparent power
| null | 0 | 28
-1
-1
-1
-1
-1
-1

## EEM_MA370_part2_v1
Name | Type | MBSize | Offset | Mode | Factor | Exponent | Unit | Min | Max | Default | Description | Info
THDU12 | uint16 | 1 | 0 | default |  | -1 | % |  |  |  | V12 THD
THDU23 | uint16 | 1 | 1 | default |  | -1 | % |  |  |  | V23 THD
THDU31 | uint16 | 1 | 2 | default |  | -1 | % |  |  |  | V23 THD
_stub | byte$6 | 3 | 3 | default
THDI1 | uint16 | 1 | 6 | default |  | -1 | % |  |  |  | I1 THD
THDI2 | uint16 | 1 | 7 | default |  | -1 | % |  |  |  | I2 THD
THDI3 | uint16 | 1 | 8 | default |  | -1 | % |  |  |  | I3 THD
| null | 0 | 9
-1
-1
-1
-1
-1
-1

## OR_WE_514_part1_v1
Name | Type | MBSize | Offset | Mode | Factor | Exponent | Unit | Min | Max | Default | Description | Info
Freq | uint16 | 1 | 0 | default |  | -2 | Hz |  |  |  | Frequency
Vrms | uint16 | 1 | 1 | default |  | -2 | V |  |  |  | Vrms
_stub | byte$14 | 7 | 2 | default
Irms | uint32 | 2 | 9 | default |  | -3 | A |  |  |  | Irms
_stub | byte$10 | 5 | 11 | default
APwr | uint32 | 2 | 16 | default |  |  | W |  |  |  | Active Power
_stub | byte$12 | 6 | 18 | default
RPwr | uint32 | 2 | 24 | default |  |  | var |  |  |  | Reactive Power
_stub | byte$12 | 6 | 26 | default
SPwr | uint32 | 2 | 32 | default |  |  | VA |  |  |  | Apparent Power
_stub | byte$12 | 6 | 34 | default
PF | uint16 | 1 | 40 | default |  | -3 |  |  |  | 0 | Power Factor
| null | 0 | 41

## OR_WE_514_part2_v1
Name | Type | MBSize | Offset | Mode | Factor | Exponent | Unit | Min | Max | Default | Description | Info
Energy | uint32 | 2 | 0 | default |  | -2 | kWh |  |  | 0 | Energy
| null | 0 | 2

## SOLIS_4G_3P_part1_v1
Name | Type | MBSize | Offset | Mode | Factor | Exponent | Unit | Min | Max | Default | Description | Info
AC_W | uint32 | 2 | 0 | default |  |  | W |  |  |  | AC Power | 3004 | 3004
DC_W | uint32 | 2 | 2 | default |  |  | W |  |  |  | DC Power | 3006 | 3006
EGY_TOT | uint32 | 2 | 4 | default |  |  | kWh |  |  |  | Total Energy | 3008 | 3008
_stub | byte$2 | 1 | 6 | default | [7 empty] | 3010 | 3010
EGY_MONTH_CUR | uint16 | 1 | 7 | default |  |  | kWh |  |  |  | This month energy | 3011 | 3011
_stub | byte$4 | 2 | 8 | default | [7 empty] | 3012..3013 | 3012
EGY_TODAY | uint16 | 1 | 10 | default |  | -1 | kWh |  |  |  | Today energy | 3014 | 3014
EGY_YESTERDAY | uint16 | 1 | 11 | default |  | -1 | kWh |  |  |  | Yesterday energy | 3015 | 3015
_stub | byte$2 | 1 | 12 | default | [7 empty] | 3016 | 3016
EGY_YEAR_CUR | uint16 | 1 | 13 | default |  |  | kWh |  |  |  | This year energy | 3017 | 3017
_stub | byte$6 | 3 | 14 | default | [7 empty] | 3018..3020 | 3018
DC_V1 | uint16 | 1 | 17 | default |  | -1 | V |  |  |  | DC V String 1 | 3021 | 3021
DC_I1 | uint16 | 1 | 18 | default |  | -1 | A |  |  |  | DC I String 1 | 3022 | 3022
DC_V2 | uint16 | 1 | 19 | default |  | -1 | V |  |  |  | DC V String 2 | 3023 | 3023
DC_I2 | uint16 | 1 | 20 | default |  | -1 | A |  |  |  | DC I String 2 | 3024 | 3024
_stub | byte$16 | 8 | 21 | default | [7 empty] | 3025..3032 | 3025
AC_V_L1 | uint16 | 1 | 29 | default |  | -1 | V |  |  |  | AC Voltage L1 | 3033 | 3033
AC_V_L2 | uint16 | 1 | 30 | default |  | -1 | V |  |  |  | AC Voltage L2 | 3034 | 3034
AC_V_L3 | uint16 | 1 | 31 | default |  | -1 | V |  |  |  | AC Voltage L3 | 3035 | 3035
AC_I_L1 | uint16 | 1 | 32 | default |  | -1 | A |  |  |  | AC Current L1 | 3036 | 3036
AC_I_L2 | uint16 | 1 | 33 | default |  | -1 | A |  |  |  | AC Current L2 | 3037 | 3037
AC_I_L3 | uint16 | 1 | 34 | default |  | -1 | A |  |  |  | AC Current L3 | 3038 | 3038
_stub | byte$4 | 2 | 35 | default | [7 empty] | 3039..3040 | 3039
INV_TEMP | uint16 | 1 | 37 | default |  | -1 | degC |  |  |  | Inverter temperature | 3041 | 3041
GRID_FREQU | uint16 | 1 | 38 | default |  | -2 | Hz |  |  |  | Grid frequency | 3042 | 3042
| null | 0 | 39

## JANITZA_B23_part1_v1
Name | Type | MBSize | Offset | Mode | Factor | Exponent | Unit | Min | Max | Default | Description | Info
V12 | float32 | 2 | 0 | default |  |  | V |  |  |  | V12 | 19006
V23 | float32 | 2 | 2 | default |  |  | V |  |  |  | V23 | 19008
V31 | float32 | 2 | 4 | default |  |  | V |  |  |  | V31 | 19010
I1 | float32 | 2 | 6 | default |  |  | A |  |  |  | I1 | 19012
I2 | float32 | 2 | 8 | default |  |  | A |  |  |  | I2 | 19014
I3 | float32 | 2 | 10 | default |  |  | A |  |  |  | I3 | 19016
_stub | byte$4 | 2 | 12 | default | [6 empty] | _stub | 19018
P1 | float32 | 2 | 14 | default |  |  | W |  |  |  | P1 | 19020
P2 | float32 | 2 | 16 | default |  |  | W |  |  |  | P2 | 19022
P3 | float32 | 2 | 18 | default |  |  | W |  |  |  | P3 | 19024
Ptot | float32 | 2 | 20 | default |  |  | W |  |  |  | Ptot | 19026
| null | 0 | 22

## EASTRON_SDM630_part1_v1
Name | Type | MBSize | Offset | Mode | Factor | Exponent | Unit | Min | Max | Default | Description | Info
_stub | byte$12 | 6 | 0 | default | [6 empty] | Frequency
IA | float32 | 2 | 6 | default |  |  | A |  |  |  | Irms L1
IB | float32 | 2 | 8 | default |  |  | A |  |  |  | Irms L2
IC | float32 | 2 | 10 | default |  |  | A |  |  |  | Irms L3
_stub | byte$80 | 40 | 12 | default
Ptot | float32 | 2 | 52 | default |  |  | W |  |  |  | Active Power
_stub | byte$16 | 8 | 54 | default
PF | float32 | 2 | 62 | default | [6 empty] | Power Factor
_stub | byte$272 | 136 | 64 | default
V12 | float32 | 2 | 200 | default |  |  | V |  |  |  | Vrms L1
V23 | float32 | 2 | 202 | default |  |  | V |  |  |  | Vrms L2
V31 | float32 | 2 | 204 | default |  |  | V |  |  | 0 | Vrms L3
_stub | byte$108 | 54 | 204 | default
Iad | float32 | 2 | 258 | default |  |  | A |  |  |  | Irms L1dem
Ibd | float32 | 2 | 260 | default |  |  | A |  |  |  | Irms L2dem
Icd | float32 | 2 | 262 | default |  |  | A |  |  |  | Irms L3dem
_stub | byte$156 | 78 | 264 | default
Energy | float32 | 2 | 342 | default |  |  | kWh |  |  | 0 | Total active energy
| null | 0 | 344 | default | [5 empty] | 0